115 Probe Error

(Check Alarm)

• Occurs during pretrip (PTI) test or probe test failed

in Chilled mode.

• Temperature difference between return air and

evaporator coil sensors is too high (1.5 C [2.7 F]

difference maximum)

• Check sensor connections. Check sensor

resistance of each sensor. Resistance must be

2,000 ohms at 25 C (77 F).

116 Probe Error

(Check Alarm)

• Occurs during pretrip (PTI) test or probe test failed

in Chilled mode.

• Temperature difference between return air and

supply air sensors is too high (0.8 C [1.5 F]

difference maximum)

• Check sensor connections. Check sensor

resistance of each sensor. Resistance must be

2,000 ohms at 25 C (77 F).