[image: image1.png]



	Hexact Ver 1.1.1

	

	General - Single

	

	Brazed Plate Heat Exchanger: B3-027-50-H

	

	Customer: 
	Date: 03-16-2012

	Reference: 
	Danfoss ref: 


	Design conditions

	

	Flow direction
	Counter Current

	
	Side 1
	
	Side 2

	Inlet temperature
	°C
	:
	86,00
	
	35,00

	Outlet temperature
	°C
	:
	50,00
	
	65,00

	Mass flow rate
	kg/s
	:
	0,2725
	
	0,0992

	Volumetric flow rate
	L/min
	:
	173,4653
	
	5,9827

	Operating Pressure - Outlet
	bar
	:
	20,593
	
	-

	

	Fluid Properties

	

	Fluid Name
	
	:
	R404A
	Water

	Reference temperature
	°C
	:
	68,00
	
	50,00

	Viscosity
	mPa-S
	:
	0,0145
	
	0,0145

	Viscosity wall
	mPa-S
	:
	0,0152
	
	0,512

	Density
	kg/m³
	:
	94,26
	
	988,85

	Specific heat capacity
	kJ/kg-K
	:
	1,243
	
	4,18

	Thermal conductivity
	W/m-K
	:
	0,020
	
	0,639

	

	Brazed Plate Heat Exchanger

	

	Heat load
	kW
	:
	
	12,44
	

	Total heat transfer area
	m²
	:
	
	1,2
	

	Mean Temperature Difference
	K
	:
	
	17,19
	

	Overall H.T.C.
	W/m²-K
	:
	
	728/603
	

	Pressure drop
	- total
	kPa
	:
	8,356
	
	0,144

	
	- channel
	kPa
	:
	8,039
	
	0,131

	
	- port
	kPa
	:
	0,317
	
	0,013

	Port hole diameter
	mm
	:
	35
	
	35

	Number of heat transfer uUnits
	
	:
	2,136
	
	1,745

	Number of channels
	
	:
	24H
	
	25H

	Total number of plates
	
	:
	
	50
	

	Over surfacing
	%
	:
	
	20,72
	

	Fouling factor
	m²-K/kW
	:
	
	0,2846
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	


[image: image2.png]



	B3-027-50-H

	[image: image3.jpg]Moy [3fjeted EEE:






	Plate Number
	50
	

	A (mm)
	129
	

	L (mm)
	25
	

	Weight (kg)
	7,7
	

	Channel Volume (L)
	Q1 Q2 side: 1,25 / Q3 Q4 side: 1,2
	

	Design pressure (bar)
	30
	

	Test Pressure (bar)
	45
	

	Design temperature (°C)
	-196 / +200
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	
	


